## Technical Information
Technical Information
SMA Modbus Interface
SMA_Modbus-TI-en-31 ¦ Version 3.1
Information on this Document
This document is a supplement to the technical descriptions "SMA Modbus® interface" and "SMA Cluster Controller Modbus® interface". It contains device-specific Modbus registers for SMA inverters with Speedwire interface. The individual sheets are named by the corresponding inverter type and firmware version. In each case a sheet contains the supported Modbus registers of a device with short descriptions. For additional information, please see the technical description referenced under "Additional Information". When directly connected to a TCP/IP network or when connected to SMA Cluster Controller, the Modbus registers of a device are accessible under the Unit ID = 3.
Additional Information
Additional information is available at www.SMA-Solar.com
Document title, Document type
SMA Modbus® Interface, technical description
SMA Cluster Controller Modbus® Interface, technical description
Legal Provisions
The information contained in this document is the property of SMA Solar Technology AG. Any publication, whether in whole or in part, requires prior written approval by SMA Solar Technology AG. Internal reproduction used solely for the purpose of product evaluation or other proper use is allowed and does not require prior approval.
Trademarks
All trademarks are recognized, even if not explicitly identified as such. A lack of identification does not mean that a product or symbol is not trademarked.
Modbus® is a registered trademark of Schneider Electric and is licensed by the Modbus Organization, Inc.
SMA SOLAR TECHNOLOGY AG
Sonnenallee 1
34266 Niestetal
Deutschland
Tel. +49 561 9522-0
Fax +49 561 9522-100
www.SMA.de
E-Mail: info@SMA.de
Copyright © 2020 SMA Solar Technology AG. All rights reserved.

## SMA Device Type Enum.
SMA Device Types
Type Designation | Device Type ID | Explanation
Sunny Boy
SB 5000SE-10 | 9225 | This sheet breaks down SMA device type enumerators to type designations.
SB 3600SE-10 | 9226 | The device type enumerators are provided by the
SB 3000TL-21 | 9074 | Modbus register address 30053 in "SMA Modbus Profile".
SB 3600TL-21 | 9165
SB 4000TL-21 | 9075
SB 5000TL-21 | 9076
SB 2500TLST-21 | 9184
SB 3000TLST-21 | 9185
SB 3500TL-JP-22 | 9162
SB 4500TL-JP-22 | 9164
SB 3000TL-US-22 | 9198
SB 3800TL-US-22 | 9199
SB 4000TL-US-22 | 9200
SB 5000TL-US-22 | 9201
SB 6000TL-US-22 | 9274
SB 7000TL-US-22 | 9275
SB 7700TL-US-22 | 9293
Sunny Tripower
STP 8000TL-10 | 9101
STP 10000TL-10 | 9067
STP 12000TL-10 | 9068
STP 15000TL-10 | 9069
STP 17000TL-10 | 9070
STP 15000TLEE-10 | 9182
STP 20000TLEE-10 | 9181
STP 10000TLEE-JP-10 | 9222
STP 12000TL-US-10 | 9194
STP 15000TL-US-10 | 9195
STP 20000TL-US-10 | 9196
STP 24000TL-US-10 | 9197
STP 30000TL-US-10 | 9310
STP 20000TLEE-JP-11 | 9271
STP 10000TLEE-JP-11 | 9272
STP 5000TL-20 | 9098
STP 6000TL-20 | 9099
STP 7000TL-20 | 9100
STP 8000TL-20 | 9103
STP 9000TL-20 | 9102
STP 10000TL-20 | 9281
STP 11000TL-20 | 9282
STP 12000TL-20 | 9283
STP 24500TL-JP-30 | 9354
STP 25000TL-JP-30 | 9311
Sunny Island
SI3.0M-11 | 9278
SI4.4M-11 | 9279
SI6.0H-11 | 9223
SI8.0H-11 | 9224

## STP nn000TL-20, PKG 2.56
SMA Modbus Profile
Modbus register address | Short description / Enumerators | Unit | Format | Type | Access | Supported hardware and firmware:
30051 | Device class: 8001 = Solar Inverters |  | U32 | ENUM | RO | Sunny Tripower
30053 | Device type: 9098 = STP 5000TL-20 9099 = STP 6000TL-20 9100 = STP 7000TL-20 9102 = STP 9000TL-20 9103 = STP 8000TL-20 9281 = STP 10000TL-20 9282 = STP 11000TL-20 9283 = STP 12000TL-20 |  | U32 | ENUM | RO | Sunny Tripower: STP 5000TL-20 / STP 6000TL-20 / STP 7000TL-20 / STP 8000TL-20 / STP 9000TL-20 / STP 10000TL-20 / STP 12000TL-20 Starting with software package: 2.55.03.R
30057 | Serial number |  | U32 | RAW | RO
30059 | Software package |  | U32 | FW | RO
30197 | Current event number |  | U32 | FIX0 | RO
30199 | Waiting time until feed-in | s | U32 | Duration | RO
30201 | Condition: 35 = Fault 303 = Off 307 = Ok 455 = Warning |  | U32 | ENUM | RO
30203 | Nominal power in Ok Mode | W | U32 | FIX0 | RO
30205 | Nominal power in Warning Mode | W | U32 | FIX0 | RO
30207 | Nominal power in Fault Mode | W | U32 | FIX0 | RO
30211 | Recommended action: 336 = Contact manufacturer 337 = Contact installer 338 = invalid 887 = none |  | U32 | ENUM | RO
30213 | Message: 886 = none |  | U32 | ENUM | RO
30215 | Fault correction measure: 885 = none |  | U32 | ENUM | RO
30217 | Grid relay/contactor: 51 = Closed 311 = Open 16777213 = Information not available |  | U32 | ENUM | RO
30219 | Derating: 557 = Temperature derating 884 = not active 16777213 = Information not available |  | U32 | ENUM | RO
30225 | Insulation resistance | Ohms | U32 | FIX0 | RO
30231 | Maximum active power device | W | U32 | FIX0 | RO
30233 | Set active power limit | W | U32 | FIX0 | RO
30247 | Current event number for manufacturer |  | U32 | FIX0 | RO
30513 | Total yield | Wh | U64 | FIX0 | RO
30517 | Daily yield | Wh | U64 | FIX0 | RO
30521 | Operating time | s | U64 | Duration | RO
30525 | Feed-in time | s | U64 | Duration | RO
30529 | Total yield | Wh | U32 | FIX0 | RO
30531 | Total yield | kWh | U32 | FIX0 | RO
30533 | Total yield | MWh | U32 | FIX0 | RO
30535 | Daily yield | Wh | U32 | FIX0 | RO
30537 | Daily yield | kWh | U32 | FIX0 | RO
30539 | Daily yield | MWh | U32 | FIX0 | RO
30541 | Operating time | s | U32 | Duration | RO
30543 | Feed-in time | s | U32 | Duration | RO
30559 | Number of events for user |  | U32 | FIX0 | RO
30561 | Number of events for installer |  | U32 | FIX0 | RO
30563 | Number of events for service |  | U32 | FIX0 | RO
30583 | Grid feed-in counter reading | Wh | U32 | FIX0 | RO
30599 | Number of grid connections |  | U32 | FIX0 | RO
30769 | DC current input [1] | A | S32 | FIX3 | RO
30771 | DC voltage input [1] | V | S32 | FIX2 | RO
30773 | DC power input [1] | W | S32 | FIX0 | RO
30775 | Power | W | S32 | FIX0 | RO
30777 | Power L1 | W | S32 | FIX0 | RO
30779 | Power L2 | W | S32 | FIX0 | RO
30781 | Power L3 | W | S32 | FIX0 | RO
30783 | Grid voltage phase L1 | V | U32 | FIX2 | RO
30785 | Grid voltage phase L2 | V | U32 | FIX2 | RO
30787 | Grid voltage phase L3 | V | U32 | FIX2 | RO
30795 | Grid current | A | U32 | FIX3 | RO
30803 | Grid frequency | Hz | U32 | FIX2 | RO
30805 | Reactive power | VAr | S32 | FIX0 | RO
30807 | Reactive power L1 | VAr | S32 | FIX0 | RO
30809 | Reactive power L2 | VAr | S32 | FIX0 | RO
30811 | Reactive power L3 | VAr | S32 | FIX0 | RO
30813 | Apparent power | VA | S32 | FIX0 | RO
30815 | Apparent power L1 | VA | S32 | FIX0 | RO
30817 | Apparent power L2 | VA | S32 | FIX0 | RO
30819 | Apparent power L3 | VA | S32 | FIX0 | RO
30825 | Operating mode of stat.V stab., stat.V stab. config.: 303 = Off 1069 = React. power/volt. char. Q(U) 1070 = Reactive power Q, direct spec. 1072 = Q specified by PV system control 1074 = cosPhi, direct specific. 1075 = cosPhi, specified by PV system control 1076 = cosPhi(P) characteristic 1984 = Reactive power/volt. char. Q(U) with meas. points 2270 = cos Phi or Q specification through optimum PV system control |  | U32 | ENUM | RO
30829 | Reactive power set value as a % | % | S32 | FIX1 | RO
30831 | cosPhi setpoint, cosPhi config., direct specif. |  | S32 | FIX2 | RO
30833 | cosPhi excit.type, cosPhi config., direct spec.: 1041 = Overexcited 1042 = Underexcited |  | U32 | ENUM | RO
30835 | Operating mode of feed-in management: 303 = Off 1077 = Active power limitation P in W 1078 = Act. power lim. as % of Pmax 1079 = Act. power lim. via PV system ctrl |  | U32 | ENUM | RO
30837 | Active power limitation P, active power configuration | W | U32 | FIX0 | RO
30839 | Active power limitation P, active power configuration | % | U32 | FIX0 | RO
30881 | Plant mains connection: 1779 = Separated 1780 = Public electricity mains 1781 = Island mains 16777213 = Information not available |  | U32 | ENUM | RO
30925 | Connection speed of SMACOM A: 302 = ------- 1720 = 10 Mbit/s 1721 = 100 Mbit/s |  | U32 | ENUM | RO
30927 | Duplex mode of SMACOM A: 302 = ------- 1726 = Half duplex 1727 = Full duplex |  | U32 | ENUM | RO
30929 | Speedwire connection status of SMACOM A: 35 = Fault 307 = Ok 455 = Warning 1725 = No connection |  | U32 | ENUM | RO
30949 | Displacement power factor |  | U32 | FIX3 | RO
30953 | Internal temperature | °C | S32 | TEMP | RO
30957 | DC current input [2] | A | S32 | FIX3 | RO
30959 | DC voltage input [2] | V | S32 | FIX2 | RO
30961 | DC power input [2] | W | S32 | FIX0 | RO
30975 | Intermediate circuit voltage | V | S32 | FIX2 | RO
30977 | Grid current phase L1 | A | S32 | FIX3 | RO
30979 | Grid current phase L2 | A | S32 | FIX3 | RO
30981 | Grid current phase L3 | A | S32 | FIX3 | RO
31017 | Current speedwire IP address |  | STR32 | UTF8 | RO
31025 | Current speedwire subnet mask |  | STR32 | UTF8 | RO
31033 | Current speedwire gateway address |  | STR32 | UTF8 | RO
31041 | Current speedwire DNS server address |  | STR32 | UTF8 | RO
31085 | Nominal power in Ok Mode | W | U32 | FIX0 | RO
31159 | Current spec. reactive power Q | VAr | S32 | FIX0 | RO
31247 | Residual current | A | S32 | FIX3 | RO
31793 | DC current input [1] | A | S32 | FIX3 | RO
31795 | DC current input [2] | A | S32 | FIX3 | RO
34113 | Internal temperature | °C | S32 | TEMP | RO
35377 | Number of events for user |  | U64 | FIX0 | RO
35381 | Number of events for installer |  | U64 | FIX0 | RO
35385 | Number of events for service |  | U64 | FIX0 | RO
40009 | Operating condition: 295 = MPP 381 = Stop 443 = Constant voltage |  | U32 | ENUM | RW
40013 | Language of the user interface: 777 = Deutsch 778 = English 779 = Italiano 780 = Español 781 = Français 782 = Ελληνικά 783 = 한국어 784 = Česky 785 = Português 786 = Nederlands 796 = Slovenski 797 = Български 798 = Polski 799 = 日本語 |  | U32 | ENUM | RW
40015 | Normalized reactive power limitation by PV system ctrl | % | S16 | FIX1 | W
40016 | Normalized active power limitation by PV system ctrl | % | S16 | FIX0 | W
40018 | Fast shut-down: 381 = Stop 1467 = Start 1749 = Full stop |  | U32 | ENUM | W
40022 | Normalized reactive power limitation by PV system ctrl | % | S16 | FIX2 | W
40023 | Normalized active power limitation by PV system ctrl | % | S16 | FIX2 | W
40024 | Dis.pow.factor that can be changed via PV system ctrl |  | U16 | FIX4 | W
40025 | Excitation type that can be changed by PV system ctrl: 1041 = Overexcited 1042 = Underexcited |  | U32 | ENUM | W
40029 | Operating status: 295 = MPP 381 = Stop 443 = Constant voltage 1392 = Fault 1393 = Waiting for PV voltage 1467 = Start 1469 = Shut down 1480 = Waiting for utilities company 2119 = Derating 16777213 = Information not available |  | U32 | ENUM | RO
40063 | Firmware version of the main processor |  | U32 | FW | RO
40065 | Firmware version of the logic component |  | U32 | FW | RO
40067 | Serial number |  | U32 | RAW | RO
40095 | Voltage monitoring upper maximum threshold | V | U32 | FIX2 | RW
40109 | Country standard set: 27 = Special setting 42 = AS4777.3 306 = Island mode 60 Hz 313 = Island mode 50 Hz 333 = PPC 438 = VDE0126-1-1 560 = EN50438 1013 = Other standard 1020 = Medium-Voltage Directive (Germany) 1199 = PPDS 7501 = RD1663/661-A 7506 = VDE0126-1-1/UTE 7510 = VDE-AR-N4105 7513 = VDE-AR-N4105-MP 7514 = VDE-AR-N4105-HP 7518 = CEI 0-21 external 7522 = NEN-EN50438 7523 = C10/11/2012 7524 = RD1699 7525 = G83/2 7526 = VFR2013 7527 = VFR2014 7528 = G59/3 7529 = SI4777_HS131_Pf 7530 = MEA2013 7531 = PEA2013 7532 = EN50438:2013 7533 = NEN-EN50438:2013 7539 = RD1699/413 7549 = AS4777.2_2015 16777213 = Information not available |  | U32 | ENUM | RO
40133 | Grid nominal voltage | V | U32 | FIX0 | RW
40135 | Nominal frequency | Hz | U32 | FIX2 | RW
40157 | Automatic speedwire configureation switched on: 1129 = Yes 1130 = No |  | U32 | ENUM | RW
40159 | Speedwire IP address |  | STR32 | IP4 | RW
40167 | Speedwire subnet mask |  | STR32 | IP4 | RW
40175 | Speedwire gateway address |  | STR32 | IP4 | RW
40185 | Maximum apparent power device | VA | U32 | FIX0 | RO
40195 | Currently set apparent power limit | VA | U32 | FIX0 | RW
40200 | Operating mode of stat.V stab., stat.V stab. config.: 303 = Off 1069 = React. power/volt. char. Q(U) 1070 = Reactive power Q, direct spec. 1072 = Q specified by PV system control 1074 = cosPhi, direct specific. 1075 = cosPhi, specified by PV system control 1076 = cosPhi(P) characteristic 1984 = Reactive power/volt. char. Q(U) with meas. points 2270 = cos Phi or Q specification through optimum PV system control |  | U32 | ENUM | RW
40204 | Reactive power set value as a % | % | S32 | FIX1 | RW
40206 | cosPhi setpoint, cosPhi config., direct specif. |  | S32 | FIX2 | RW
40208 | cosPhi excit.type, cosPhi config., direct spec.: 1041 = Overexcited 1042 = Underexcited |  | U32 | ENUM | RW
40210 | Operating mode of feed-in management: 303 = Off 1077 = Active power limitation P in W 1078 = Act. power lim. as % of Pmax 1079 = Act. power lim. via PV system ctrl |  | U32 | ENUM | RW
40212 | Active power limitation P, active power configuration | W | U32 | FIX0 | RW
40214 | Active power limitation P, active power configuration | % | U32 | FIX0 | RW
40216 | Operating mode of active power reduction in case of overfrequency P(f): 303 = Off 1132 = Linear gradient 3175 = Linear gradient of the maximum active power |  | U32 | ENUM | RW
40218 | Difference between starting frequency and grid frequency, linear instantaneous power gradient configuration | Hz | U32 | FIX2 | RW
40220 | Difference between reset frequency and grid frequency, linear instantaneous power gradient configuration | Hz | U32 | FIX2 | RW
40222 | cosPhi at start point, cosPhi(P) char. config. |  | U32 | FIX2 | RW
40224 | Excit. type at start point, cosPhi(P) char. conf.: 1041 = Overexcited 1042 = Underexcited |  | U32 | ENUM | RW
40226 | cosPhi at end point, cosPhi(P) char. config. |  | U32 | FIX2 | RW
40228 | Excit. type at end point, cosPhi(P) char. config.: 1041 = Overexcited 1042 = Underexcited |  | U32 | ENUM | RW
40230 | Act. power at start point, cosPhi(P) char. config. | % | U32 | FIX0 | RW
40232 | Act. power at end point, cosPhi(P) char. config. | % | U32 | FIX0 | RW
40234 | Active power gradient | % | U32 | FIX0 | RW
40238 | Active power gradient, linear instantaneous power gradient configuration | % | U32 | FIX0 | RW
40240 | Activation of stay-set indicator function, linear instantaneous power gradient configuration: 303 = Off 308 = On |  | U32 | ENUM | RW
40242 | Active power gradient after reset frequency, linear instantaneous power gradient configuration | % | U32 | FIX0 | RW
40244 | Reactive current droop, full dynamic grid support configuration: 1233 = SDLWindV 1020 = Medium-Voltage Directive (Germany) |  | U32 | ENUM | RW
40250 | Operating mode of dynamic grid support, dynamic grid support configuration: 1265 = Limited dynamic grid support 1264 = Full dynamic grid support |  | U32 | ENUM | RW
40252 | Lower limit, voltage dead band, full dynamic grid support configuration | % | S32 | FIX0 | RW
40254 | Upper limit, voltage dead band, full dynamic support configuration | % | U32 | FIX0 | RW
40256 | PWM inverse voltage, dynamic grid support configuration | % | U32 | FIX0 | RW
40258 | PWM inversion delay, dynamic grid support configuration | s | U32 | FIX2 | RW
40260 | Characteristic curve number of the PV system control procedure P(U) |  | U32 | FIX0 | RW
40428 | Frequency monitoring median maximum threshold | Hz | U32 | FIX2 | RW
40430 | Frq. monitoring median max. threshold trip. time | ms | U32 | FIX0 | RW
40432 | Frequency monitoring lower maximum threshold | Hz | U32 | FIX2 | RW
40434 | Frq. monitoring lower max. threshold trip. time | ms | U32 | FIX0 | RW
40436 | Frequency monitoring upper minimum threshold | Hz | U32 | FIX2 | RW
40438 | Frq. monitoring upper min. threshold trip. time | ms | U32 | FIX0 | RW
40440 | Frequency monitoring median minimum threshold | Hz | U32 | FIX2 | RW
40442 | Frq. monitoring median min. threshold trip. time | ms | U32 | FIX0 | RW
40446 | Voltage monitoring upper max. threshold trip. time | ms | U32 | FIX3 | RW
40448 | Voltage monitoring median maximum threshold | V | U32 | FIX2 | RW
40450 | Voltage monitoring median max. threshold trip.time | ms | U32 | FIX0 | RW
40452 | Voltage monitoring lower maximum threshold | V | U32 | FIX2 | RW
40456 | Voltage monitoring lower max. threshold trip. time | ms | U32 | FIX0 | RW
40458 | Voltage monitoring lower minimum threshold | V | U32 | FIX2 | RW
40462 | Voltage monitoring lower min. threshold trip. time | ms | U32 | FIX0 | RW
40464 | Voltage monitoring of median minimum threshold | V | U32 | FIX2 | RW
40466 | Voltage monitoring median min. threshold trip.time | ms | U32 | FIX0 | RW
40472 | Reference voltage, PV system control | V | U32 | FIX0 | RW
40474 | Reference correction voltage, PV system control | V | S32 | FIX0 | RW
40482 | Reactive power gradient | % | U32 | FIX0 | RW
40484 | Activation of active power gradient: 303 = Off 308 = On |  | U32 | ENUM | RW
40490 | Reactive power gradient, reactive power/voltage characteristic curve configuration Q(U) | % | U32 | FIX1 | RW
40497 | MAC address |  | STR32 | UTF8 | RO
40513 | Speedwire DNS server address |  | STR32 | IP4 | RW
40575 | Operating mode of multifunction relay: [1] 258 = Switching status grid relay 1341 = Fault indication 1342 = Fan control 1343 = Self-consumption 1349 = Control via communication 1359 = Battery bank |  | U32 | ENUM | RW
40631 | Device name |  | STR32 | UTF8 | RW
40789 | Communication version |  | U32 | REV | RO
40809 | Revision status of the logic component |  | U32 | FIX0 | RW
40915 | Set active power limit | W | U32 | FIX0 | RW
40997 | Hysteresis voltage, dynamic grid support configuration | % | U32 | FIX0 | RW
40999 | Setpoint cos(phi) as per EEI convention |  | S32 | FIX4 | W
41017 | Adjustment time of characteristic operating point, conf. of grid integr. char. 1 | s | U32 | FIX1 | RW
41019 | Decrease ramp, conf. of grid integr. char. 1 | % | U32 | FIX1 | RW
41021 | Increase ramp, conf. of grid integr. char. 1 | % | U32 | FIX1 | RW
41023 | Number of points to be used, conf. of grid integr. char. 1 |  | U32 | FIX0 | RW
41025 | X-axes reference, conf. of grid integration char. 1: 1975 = Voltage in V 1976 = Voltage in percentages of Un |  | U32 | ENUM | RW
41027 | Y-axes reference, conf. of grid integration char. 1: 1977 = Var in percentages of Pmax 1978 = Power in percentages of Pmax 1979 = Power in percentages of frozen active power |  | U32 | ENUM | RW
41029 | X value 1, conf. of grid integr. char. 1 |  | S32 | FIX3 | RW
41031 | Y value 1, conf. of grid integr. char. 1 |  | S32 | FIX3 | RW
41033 | X value 2, conf. of grid integr. char. 1 |  | S32 | FIX3 | RW
41035 | Y value 2, conf. of grid integr. char. 1 |  | S32 | FIX3 | RW
41037 | X value 3, conf. of grid integr. char. 1 |  | S32 | FIX3 | RW
41039 | Y value 3, conf. of grid integr. char. 1 |  | S32 | FIX3 | RW
41041 | X value 4, conf. of grid integr. char. 1 |  | S32 | FIX3 | RW
41043 | Y value 4, conf. of grid integr. char. 1 |  | S32 | FIX3 | RW
41045 | X value 5, conf. of grid integr. char. 1 |  | S32 | FIX3 | RW
41047 | Y value 5, conf. of grid integr. char. 1 |  | S32 | FIX3 | RW
41049 | X value 6, conf. of grid integr. char. 1 |  | S32 | FIX3 | RW
41051 | Y value 6, conf. of grid integr. char. 1 |  | S32 | FIX3 | RW
41053 | X value 7, conf. of grid integr. char. 1 |  | S32 | FIX3 | RW
41055 | Y value 7, conf. of grid integr. char. 1 |  | S32 | FIX3 | RW
41057 | X value 8, conf. of grid integr. char. 1 |  | S32 | FIX3 | RW
41059 | Y value 8, conf. of grid integr. char. 1 |  | S32 | FIX3 | RW
41065 | Adjustment time of char. operating point, conf. of grid integration char. 2 | s | U32 | FIX1 | RW
41067 | Decrease ramp, conf. of grid integration char. 2 | % | U32 | FIX1 | RW
41069 | Increase ramp, conf. of grid integration char. 2 | % | U32 | FIX1 | RW
41071 | Number of points to be used, conf. of grid integr. char. 2 |  | U32 | FIX0 | RW
41073 | Input unit, conf. of grid integration char. 2: 1975 = Voltage in V 1976 = Voltage in percentages of Un |  | U32 | ENUM | RW
41075 | Output frequency, conf. of grid integration char. 2: 1977 = Var in percentages of Pmax 1978 = Power in percentages of Pmax 1979 = Power in percentages of frozen active power |  | U32 | ENUM | RW
41077 | X value 1, conf. of grid integr. char. 2 |  | S32 | FIX3 | RW
41079 | Y value 1, conf. of grid integr. char. 2 |  | S32 | FIX3 | RW
41081 | X value 2, conf. of grid integr. char. 2 |  | S32 | FIX3 | RW
41083 | Y value 2, conf. of grid integr. char. 2 |  | S32 | FIX3 | RW
41085 | X value 3, conf. of grid integr. char. 2 |  | S32 | FIX3 | RW
41087 | Y value 3, conf. of grid integr. char. 2 |  | S32 | FIX3 | RW
41089 | X value 4, conf. of grid integr. char. 2 |  | S32 | FIX3 | RW
41091 | Y value 4, conf. of grid integr. char. 2 |  | S32 | FIX3 | RW
41093 | X value 5, conf. of grid integr. char. 2 |  | S32 | FIX3 | RW
41095 | Y value 5, conf. of grid integr. char. 2 |  | S32 | FIX3 | RW
41097 | X value 6, conf. of grid integr. char. 2 |  | S32 | FIX3 | RW
41099 | Y value 6, conf. of grid integr. char. 2 |  | S32 | FIX3 | RW
41101 | X value 7, conf. of grid integr. char. 2 |  | S32 | FIX3 | RW
41103 | Y value 7, conf. of grid integr. char. 2 |  | S32 | FIX3 | RW
41105 | X value 8, conf. of grid integr. char. 2 |  | S32 | FIX3 | RW
41107 | Y value 8, conf. of grid integr. char. 2 |  | S32 | FIX3 | RW
41121 | Set country standard: 42 = AS4777.3 306 = Island mode 60 Hz 313 = Island mode 50 Hz 333 = PPC 438 = VDE0126-1-1 560 = EN50438 1013 = Other standard 1020 = Medium-Voltage Directive (Germany) 1199 = PPDS 7501 = RD1663/661-A 7506 = VDE0126-1-1/UTE 7510 = VDE-AR-N4105 7513 = VDE-AR-N4105-MP 7514 = VDE-AR-N4105-HP 7518 = CEI 0-21 external 7522 = NEN-EN50438 7523 = C10/11/2012 7524 = RD1699 7525 = G83/2 7526 = VFR2013 7527 = VFR2014 7528 = G59/3 7529 = SI4777_HS131_Pf 7530 = MEA2013 7531 = PEA2013 7532 = EN50438:2013 7533 = NEN-EN50438:2013 7539 = RD1699/413 7549 = AS4777.2_2015 |  | U32 | FUNKTION_SEC | RW
41123 | Min. voltage for reconnection | V | U32 | FIX2 | RW
41125 | Max. voltage for reconnection | V | U32 | FIX2 | RW
41127 | Lower frequency for reconnection | Hz | U32 | FIX2 | RW
41129 | Upper frequency for reconnection | Hz | U32 | FIX2 | RW
41131 | Minimum voltage input [1] | V | U32 | FIX2 | RW
41133 | Minimum voltage input [2] | V | U32 | FIX2 | RW
41155 | Start delay input [1] | s | U32 | FIX0 | RW
41157 | Start delay input [2] | s | U32 | FIX0 | RW
41169 | Minimum insulation resistance | Ohms | U32 | FIX0 | RW
41171 | Set total yield | kWh | U32 | FIX0 | RW
41173 | Set total operating time at grid connection point | h | U32 | Duration | RW
41193 | Operating mode for absent active power limitation: 2506 = Values maintained 2507 = Use fallback setting |  | U32 | ENUM | RW
41195 | Timeout for absent active power limitation | s | U32 | Duration | RW
41197 | Fallback act power lmt P in % of WMax for absent act power lmt | % | U32 | FIX2 | RW
43090 | Login with Grid Guard-Code |  | U32 | FIX0 | RW